STATUTORY RULES 2026

S.R. No.

Building Act 1993

Plumbing Amendment (Water Efficiency) Regulations 2026

The Governor in Council makes the following Regulations:

Dated:

Responsible Minister:

Harriet Shing, Minister for Housing and Building

# 1  Objective

The objective of these Regulations is to amend the Plumbing Regulations 2018 to prescribe minimum requirements for water efficiency for certain fixtures and fittings of buildings.

# 2  Authorising provisions

These Regulations are made under sections 221ZZZV and 262 of the Building Act 1993.

# 3  Principal Regulations

In these Regulations, the Plumbing Regulations 2018 are called the Principal Regulations.

# 4  Commencement

These Regulations come into operation on [to be confirmed].

# 5  Definitions

In regulation 5 of the Principal Regulations—

(a) 	insert the following definition–

"WELS scheme has the same meaning as in the Water Efficiency Labelling and Standards Act 2005";

(b)	for the definition of water efficient shower head substitute—

"water efficient shower head means a shower head with a WELS scheme water efficiency rating of 4 stars or greater;";

(c)	in the definition of water supply work, for "regulation 30." substitute "regulation 30;”.

# 8  New Subdivision 1 heading inserted in Division 7 of Schedule 2

After the heading to Division 7 of Schedule 2 to the Principal Regulations insert—

"Subdivision 1—Cooling towers".

# 9  New Subdivision 2 of Division 7 of Schedule 2 inserted

After clause 7 of Schedule 2 to the Principal Regulations insert—

"Subdivision 2 —Water efficiency requirements—water supply services

7A  Application

This Subdivision applies despite any provision to the contrary in the PCA.

7B  Water efficiency requirements—water supply services

- For the purposes of regulation 31, the following standards apply to water supply work that is the installation of a water service in a building—

- a WELS scheme water efficiency rating of 4 stars or greater for the following—

- a tap for a kitchen sink;

- a tap for a laundry trough;

- a shower head;

- a cistern or flushing valve connected to a water closet, other than a vacuum water closet pan;

- a WELS scheme water efficiency rating of 5 stars or greater for the following—

- a tap for a bathroom basin in a Class 1 building or Class 2 building;

- a cistern or flushing valve connected to a urinal;

- a WELS scheme water efficiency rating of 6 stars or greater for a tap for a bathroom basin in a building other than a Class 1 or Class 2 building.

7C  Water services—exceptions for existing buildings

- A requirement specified in clause 7B in relation to a water service does not apply to a part of a water service in an existing building if—

- the requirement cannot be complied with because of the age, nature or structure of that part of the water service; or

- complying with the requirement would impair the effective operation of the water service in the building.

- A part in a water service that is exempt from a requirement in clause 7B because of the application of subclause (1) must have —

- a WELS scheme water efficiency rating of 3 stars or greater; and

- the highest WELS scheme water efficiency rating that can be used for that part in that water supply service while still enabling the water supply service to operate effectively.

# 10  Clause 8 revoked and New Subdivision 3 of Division 7 of Schedule 2 inserted

For clause 8 of Schedule 2 to the Principal Regulations substitute—

"Subdivision 3—standards for  rainwater tanks

8  Application

This Subdivision applies despite any provision to the contrary in the PCA.

8A  Standards where rainwater tank installed—interchange device

- This clause applies if a reticulated water supply from a network utility operator is connected, or proposed to be connected, to a building where a rainwater tank is installed as a water service for the building.

- An automatic or manual interchange device that allows alternate use of water from the rainwater tank or the reticulated water supply must be installed to ensure that there is a continual supply of water to the building.

# 11  New Subdivision 4 heading inserted in Division 7 of Schedule 2

Before clause 12 of Schedule 2 to the Principal Regulations insert—

"Subdivision 4—Standards relating to water closets".

═════════════

# Endnotes

1 Reg 4: S.R. No. 149/2018 as amended by S.R. Nos. 149/2018, 41/2019, 122/2022, 102/2023, 122/2023 and 2/2024.